Table of Contents

# Zero Missed Hazards Is Not a Safety Claim: Evaluating Machine-Learning Gas-Hazard Monitoring Beyond Accuracy

Benjamin C. Nweke^a,b,*, Gholamreza Ramezan^b, Soheil Saraji^a

^a Subsurface Energy and Digital Innovation Center (SEDI), Department of Energy and Petroleum Engineering, University of Wyoming, 1000 E. University Ave., Laramie, WY 82071, USA ^b Fides Innova Labs, Vancouver, BC, Canada

* Corresponding author: bnweke@uwyo.edu

Prepared for submission to SPE Journal, Data Science and Engineering Analytics.

Suggested running head: Zero Missed Hazards Is Not a Safety Claim

## Summary

A fixed gas detector at a wellpad or a compressor station will generate far more abnormal indications in a week than anyone can act on. That is the practical problem. Knowing which gas is present matters less than knowing what to do about it, and the evidence available at the moment of decision is usually partial, sometimes stale, and occasionally wrong. Machine-learning work on gas detection is nevertheless ranked almost entirely by classification accuracy, which says nothing about the two quantities that decide whether a monitoring system is safe to install: how often a hazard draws no response at all, and how often clean air draws a high-severity one.

We evaluated a monitoring pipeline (thermal-image classification, normal-only anomaly scoring, cost-sensitive action assignment, and a locally generated natural-language explanation) against a broader metric set. The benchmark is the public MultimodalGasData corpus (Narkhede et al. 2022), split by a leakage-controlled block-wise holdout with a 20-window embargo. One caveat needs stating up front: the corpus contains incense smoke, alcohol-based vapor and a mixture of the two, not hydrocarbons. What follows characterizes evaluation methodology on a representative metal-oxide array. It is not a field performance estimate, and we would resist anyone reading it as one.

Eleven models were trained under a single protocol: tree ensembles, kernel methods, feedforward and recurrent networks, offline reinforcement learning, a depth-3 threshold rule, and classical sequential change detection. Four things came out of it.

In distribution, the metric set does not separate anything. Ten multiclass models sit inside 4.7 accuracy points of one another (0.930 to 0.977), a spread this design cannot resolve, and every one of them except gradient boosting records no observed missed hazards, escalation adequacy of 1.000, and no observed high-severity false alarms. Pooled over five seeds those zeros bound the underlying rates at 0.095% and 0.189% respectively, which is as far as 3,160 hazardous and 1,580 clean windows can take them. A three-level decision tree on seven raw sensor readings matches all of them on safety behavior.

Hold one hazardous class out of training, though, and the same models spread across two orders of magnitude. A multilayer perceptron missed 9.49% of unseen Smoke windows (95% Clopper-Pearson upper bound 10.05%) where four other models were bounded at 0.038%. Nothing in the in-distribution table anticipates that, and the correlation between in-distribution accuracy and out-of-distribution miss rate is essentially absent (Pearson r = +0.12).

The more uncomfortable finding concerns the miss metric itself. On unseen Mixture, seven of eight models were bounded below 2.9% on missed hazards and would pass any review conducted on that basis. Their escalation adequacy ranged from 0.5% to 100%, a factor of about 198. A support-vector classifier missed 0.03% of hazardous windows while escalating 0.5% of them, answering roughly 99.5% with “increase sampling” or “request verification.” No operator is notified by either action, and the miss metric scores the whole thing as success.

Cost asymmetry, swept from 1:1 to 20:1, changed neither missed-hazard rate (zero throughout) nor escalation adequacy (1.000 throughout), and cost accuracy above 6:1. On a benchmark this separable there appears to be no error surface for a safety objective to reshape.

Under graded sensor loss three distinct failure modes appear, and each single metric certifies a different model as safe. With all seven channels removed, the cost-weighted policy and the threshold rule record no observed miss and full escalation by alarming on everything, reaching a 100% false-alarm rate, or 1,000 high-severity alarms per 1,000 clean windows. Expressed per unit time this depends on a duty cycle the corpus does not record, so we report the per-window quantity throughout. Gradient boosting holds zero false alarms and misses 60% of hazards. Losing a single sensor of seven is already enough to take the cost-weighted policy from zero to 117 alarms per 1,000 windows, while leaving the random forest untouched.

Our conclusion is narrower than a claim about any particular model. Missed-hazard rate with a confidence bound, escalation adequacy, false-alarm burden expressed in alarm-management units, and the degradation of all three under sensor loss and drift should be reported together, because on this corpus each of them taken alone picks a different winner.

Keywords: gas-hazard monitoring; safety-relevant evaluation; cost-sensitive learning; distribution shift; alarm management; sensor degradation; anomaly detection; explainable AI

## 1. Introduction

Serious process-safety incidents are rarely preceded by silence. The warning is usually there, spread across several indications, and simply never converted into action in time. In the eleven minutes before the Milford Haven refinery explosion the control-room operator received 275 alarms (Goel et al. 2017). Sensing was not the failure. Turning what was sensed into a decision was.

The same shape of problem shows up at upstream and midstream facilities. Wellpads, tank batteries, compressor stations and gas plants carry fixed point-gas detectors, often low-cost metal-oxide-semiconductor (MOX) elements, feeding alarm systems that in a good many installations already run at or above the long-term average rates industry guidance treats as manageable for a single operator (EEMUA 2013; ISA 2016). Add to that the growing obligation to find and act on fugitive hydrocarbon release, where the response is at once a safety action and an emissions action. In both settings the operational question is not really “what gas is this.” It is closer to “what should be done in the next minute, and how sure do we need to be before doing it.”

Machine learning has been applied heavily to the first question and hardly at all to the second. Gas-detection models get ranked by classification accuracy, and on the established benchmarks that ranking has flattened out: reported accuracies on the corpus used here run from roughly 93% to 99.7% across more than ten peer-reviewed studies (Narkhede et al. 2021; Faleh and Kachouri 2023; El Barkani et al. 2024; Sharma et al. 2024; Zhang and Zhang 2025). Once a benchmark saturates, small differences between leading methods stop carrying information about deployment. The interesting question becomes what the accuracy number is failing to see.

### 1.1 A symmetric metric on an asymmetric problem

Monitoring errors are not interchangeable, and no single scalar orders them sensibly:

- A hazardous condition that draws no response gives up the whole intervention window.

- A hazardous condition that draws a sub-alarm response, say increased sampling or a request for verification, keeps part of that window but notifies nobody. It is not the same as a correct escalation, although a miss metric will treat it as though it were.

- A clean condition that draws a high-severity response spends operator attention, and at sufficient rate it degrades the alarm system that later hazards depend on (Laberge et al. 2014).

- A hazardous condition that draws the wrong high-severity response is, in most operating regimes, almost as good as the right one.

A model ranked first on accuracy can be ranked last on any of these, and the accuracy table gives no hint of which. We had assumed going in that the differences would be modest. They were not.

### 1.2 What is settled and what is not

Most of the component technology is mature. Reconstruction-based sequence models trained only on normal operation have been the default unsupervised approach to multivariate sensor anomaly detection since Malhotra et al. (2016), with field-validated applications in natural-gas pipeline monitoring (Liang et al. 2024). Vision models classify thermal and optical gas signatures fast enough for embedded hardware (Korjani et al. 2024; Jocher et al. 2023). Cost-sensitive learning has a clean formal account of unequal error costs (Elkan 2001). Fusing thermal imagery with MOX arrays improves classification relative to either alone (Narkhede et al. 2021, 2022). Compact language models make local explanation feasible without sending monitoring data off site (Dehnaw et al. 2024).

What is not settled is how any of this behaves when ranked by something other than accuracy. Four questions in particular:

RQ1. Does accuracy-ranked model selection survive a missed-hazard criterion?

RQ2. Do models that agree in distribution still agree when the hazard is one they were never trained on? That matters, because a detector in service will eventually meet a release it has not seen.

RQ3. Is missed-hazard rate itself enough, or can it be satisfied by under-response that a miss count never registers?

RQ4. Do any of these behaviors survive the sensor faults a fixed detector actually meets in service, or do they only hold on clean data?

Section 4.2 addresses RQ1, Section 4.3 addresses RQ2 and RQ3, and Section 4.6 addresses RQ4. Sections 4.4, 4.5 and 4.7 are supporting evidence rather than answers to any of the four.

### 1.3 What we contribute

An evaluation protocol. A leakage-controlled block-wise holdout with an explicit embargo and a seed-varying block position; a five-level action target that keeps missed hazard, under-escalation and high-severity false alarm apart; leave-one-class-out (LOCO) evaluation against an unseen hazard; a graded perturbation suite covering additive noise, calibration drift and channel loss at five to seven severities; and Clopper-Pearson bounds on every zero count. To the best of our knowledge we did not find a prior study combining these evaluation elements on a MOX gas-detection benchmark, though we make no claim to have searched exhaustively.

Evidence that accuracy ranking says little about safety behavior. Ten multiclass models spanning very different inductive biases span 4.7 accuracy points in distribution, are indistinguishable there on every safety metric we report, and then separate by more than two orders of magnitude on missed-hazard rate once the hazard is unseen.

Evidence that missed-hazard rate is necessary but not sufficient. On an unseen hazardous class, models with miss rates bounded below 2.9% differ by roughly 198 times in escalation adequacy, and the group with the lowest miss rates contains both the best and among the worst escalators.

Two negative results, reported rather than buried. Cost asymmetry produced no measurable change in missed-hazard rate or escalation adequacy at any ratio from 1:1 to 20:1, and hurt accuracy past 6:1. Separately, a deterministic label-function reference hits the accuracy ceiling by construction, which means any benefit from a learned policy on this corpus has to come from degraded conditions rather than nominal ones.

Comparators a facility would recognize. A depth-3 decision tree on seven raw sensor channels and a CUSUM sequential detector run under the identical protocol, so the learned models are measured against something closer to current practice than to another neural network.

We are not claiming to advance the classification state of the art here, and we are not convinced that would be worth doing. The benchmark is saturated. What remains open is what the saturated numbers miss.

## 2. Background and Related Work

### 2.1 Detection, and the gap between an indication and a decision

Gas-hazard detection rests on a well-developed base of hardware and software methods (Murvay and Silea 2012; Adegboye et al. 2019). On the hardware side, distributed acoustic and fiber-optic sensing, vapor sensing and negative-pressure-wave detection. On the software side, real-time transient modeling, mass balance, statistical analysis and model-based diagnostics (Zhang et al. 2013; Bustnes et al. 2011). These have improved identification and localization considerably, and their weak spot is usually uneven performance under real operating conditions rather than any absence of capability (Han and Kim 2014).

For our argument a different limitation matters more. All of them stop at a leak indication, a location estimate or a concentration estimate. Those outputs are necessary for loss prevention, but they are not response decisions, and the literature evaluating them does not ask whether the downstream response would have been adequate.

### 2.2 Anomaly scores as evidence, not verdicts

Since Malhotra et al. (2016), reconstruction-based sequence models trained only on normal operation have been the standard unsupervised route to multivariate sensor anomaly detection, and they have been used in pipeline monitoring with field validation (Liang et al. 2024). Their appeal for safety work is obvious: no labeled examples of every hazardous condition are needed.

An anomaly score is still an intermediate quantity, though. It says behavior has departed from baseline. It does not say what to do, and nothing about the training procedure calibrates it to hazard severity. Any use of such a score inside a safety path carries an obligation to show that it ranks hazard monotonically, and the literature rarely discharges that obligation. We test it directly in Section 4.1, and the answer is only a partial yes.

### 2.3 A saturated benchmark

MultimodalGasData pairs thermal frames with a seven-channel MOX array, and the original work showed that fusing the two beats either alone (Narkhede et al. 2021, 2022). It has since become a standard benchmark, and the reported accuracies have converged: 97.0% (Narkhede et al. 2021), 93.0% (Faleh and Kachouri 2023), 91.7% (El Barkani et al. 2024), 99.7% (Sharma et al. 2024), 99.7% (Zhang and Zhang 2025).

Two features of that literature bear on what follows. First, those figures appear to be computed on random splits over overlapping sliding windows drawn from a single recording session. Dennler et al. (2022) showed on a similarly structured MOX corpus that this conflates recording time with class identity, and flagged a sizeable body of published work for re-evaluation; Vergara et al. (2012) had already documented how far MOX response drifts over long horizons. Second, and more to the point, none of these studies reports a safety-relevant quantity. Not missed-hazard rate, not escalation adequacy, not false-alarm burden, not behavior under sensor loss. The benchmark has saturated on a metric that does not discriminate deployment fitness.

### 2.4 Cost-sensitive learning

That error costs are unequal, and that classifiers ought to be trained accordingly, has had a clean formal treatment since Elkan (2001), and cost-sensitive reweighting is now routine practice. What gets reported far less often is whether a given asymmetry actually moved the specific error it was introduced to suppress. Section 4.4 runs that test and returns a negative answer, one we suspect generalizes to any saturated, well-separated benchmark.

### 2.5 Coordination layers and operator-facing explanation

Systems that coordinate several specialized models toward a larger task have been applied in the energy sector to well-construction assistance, completions optimization and enterprise modeling (Sabbagh et al. 2024; Santiago et al. 2025; Jessen and Roshchin 2025). Those are analytical and advisory settings rather than real-time monitoring, and their evaluation criteria differ accordingly.

Explanation matters for operator-facing safety systems because trust, review and post-incident accountability all depend on it. It also brings a hazard of its own. A language model can produce an explanation that reads fluently and does not match the decision it claims to explain, which in a control room is worse than offering nothing. Our response to that is architectural, and we describe it in Section 3.3.

### 2.6 Where this study sits

Table 1 lists representative prior work with the evaluation gap each leaves open.

| Study | Area | Contribution | Evaluation gap addressed here |
| --- | --- | --- | --- |
| Malhotra et al. (2016) | Anomaly detection | Reconstruction-error scoring for multivariate streams | Score not calibrated to hazard severity; no response mapping |
| Liang et al. (2024) | Anomaly detection | Field-validated normal-only leak detection | Stops at detection; downstream response unevaluated |
| Korjani et al. (2024) | Computer vision | High detection rates on optical gas imaging | Degraded-sensing behavior not treated as a safety metric |
| Narkhede et al. (2021, 2022) | Multimodal sensing | Thermal and MOX fusion improves classification; public corpus | Classification accuracy only; random split over overlapping windows |
| Sharma et al. (2024); Zhang and Zhang (2025) | Multimodal classification | State-of-the-art accuracy on this corpus | No missed-hazard, escalation, false-alarm or degradation reporting |
| Dennler et al. (2022) | Benchmark methodology | Shows drift-induced leakage in MOX benchmarks | Motivates, but does not supply, a safety-relevant metric set |
| Elkan (2001) | Cost-sensitive learning | Formal account of unequal error costs | Effectiveness on a saturated benchmark untested |
| Sabbagh et al. (2024) | Multi-agent systems | Coordination improves answer quality | Analytical workflow, not real-time monitoring |

Table 1. Representative prior work and the evaluation gap each leaves open.

Our contribution lives in that right-hand column. It is not a new architecture. It is evidence about what the usual evaluation of these architectures fails to reveal.

## 3. Methodology

### 3.1 Corpus and preprocessing

The public MultimodalGasData corpus (Narkhede et al. 2022; Mendeley Data, CC BY 4.0) pairs a seven-channel MQ-series MOX array with synchronized 206 by 156 thermal frames from a Seek Compact camera. There are 6,400 labeled samples in four classes of 1,600: clean air (NoGas), incense smoke (Smoke), alcohol-based deodorant vapor (Perfume), and a smoke and vapor mixture (Mixture). Table 2 lists the array.

| Sensor | Commonly associated target gases (nominal sensitivity) |
| --- | --- |
| MQ-2 | LPG, butane, methane, smoke |
| MQ-3 | Alcohol, ethanol, organic vapors |
| MQ-5 | LPG, natural gas |
| MQ-6 | LPG, butane, iso-butane |
| MQ-7 | Carbon monoxide |
| MQ-8 | Hydrogen |
| MQ-135 | Air-quality indicators including NH₃, benzene, NOₓ and CO₂ |

Table 2. Composition of the MOX array. The right-hand column lists the gases each element is nominally marketed as sensitive to. It should not be read as a selectivity claim. MOX elements respond broadly and cross-sensitively, so a reading on MQ-2 is evidence of a reducing-gas response rather than of methane specifically, and no single channel identifies a gas on its own. The array is informative because the seven responses differ in relative magnitude, not because any one of them is selective.

Two properties of the corpus shaped everything downstream, and we would rather state them here than tuck them into a limitations section.

The analytes are laboratory surrogates. Incense smoke and alcohol-based vapor exercise the MOX transduction mechanism, the cross-sensitivity structure of the array, and its baseline drift, all of which a facility detector meets in service. They do not establish detection performance for methane or anything heavier. Every result below characterizes evaluation methodology on a representative MOX array.

The four classes were recorded as four contiguous blocks inside a single session of roughly 90 minutes. Within-session baseline drift is therefore confounded with class identity, which is exactly the structure Dennler et al. (2022) showed inflates reported accuracy on MOX benchmarks under a randomized split. The split we use is a response to that, not a housekeeping choice.

Windowing. Seven-channel readings were formed into sliding windows of length 20, each labeled by its final reading. Windows spanning a class boundary are discarded, so no window mixes two classes. That leaves 6,324 windows, 1,581 per class.

Split. Consecutive windows share 19 of 20 raw rows, so a random split drops near-duplicates into both partitions. A plain sequential split is no better, because the corpus is block-ordered by class. We use a block-wise holdout instead: inside each class block a contiguous 20% forms the test partition, separated from the training segments by an embargo of G = 20 windows, so no training window shares a raw row with any test window (Fig. 1). The position of the held-out block moves with the run seed, which means the dispersion we report includes data-partition variance and not just model-initialization variance (Bouthillier et al. 2021). The result is 4,980 training and 1,264 test windows, 316 per class. Feature scaling and anomaly normalization are fitted on the training partition only, then applied without refitting.

Fig. 1. Corpus layout and the leakage-controlled split. Each class occupies a contiguous block of 1,581 windows. A contiguous 20% is held out, with a 20-window embargo on each side, and the position of that block is drawn from the run seed.

### 3.2 The monitoring pipeline

The pipeline, which we call ARXIS, has five parts. At each inference cycle it takes a thermal image Iₜ and a sensor window Xₜ ∈ ℝ^(20×7) and returns a safety action aₜ ∈ {0, …, 4} plus an explanation Eₜ. A perception component classifies the thermal image. An anomaly component scores the sensor window by reconstruction error against a normal-only model. A coordination component assembles the decision state. A decision component maps that state to an action. A reasoning component writes the operator-facing explanation.

The pipeline is advisory, and we want to be explicit about that. It sits in the alarm-management and operator-support layer and does not actuate anything. The action labeled Emergency Shutdown is a recommendation that the operator start the facility’s existing ESD procedure. It does not command a trip. The safety instrumented function stays independent, deterministic and separately verified, which keeps the arrangement consistent with the independence expected of separate protection layers under layer-of-protection analysis. We are deliberately not making a claim about what IEC 61511 (IEC 2016) does or does not permit for learned components, since that is a certification question outside the scope of this study. The architectural point is narrower and does not depend on it: the model recommends an action, it does not command a trip, and the protective function is implemented, verified and actuated independently of anything reported here. All results below were obtained with the pipeline in that position, and removing it entirely leaves the facility’s protective function intact. We treat this as a design requirement rather than a caveat. A single learned component selecting across both the alarm layer and the shutdown layer would collapse two protection layers into one common-cause element, and we do not see a defensible way around that.

Fig. 2. The pipeline. Thermal evidence reaches the perception and explanation paths but never the decision state, and the language model sits downstream of an action it cannot alter.

| Action | Label | Operational response |
| --- | --- | --- |
| 0 | Monitor | Routine monitoring, no operator notification |
| 1 | Increase sampling | Elevated scan frequency and event logging |
| 2 | Request verification | Secondary sensor check and event logging; no alarm is raised |
| 3 | Raise alarm | Automated alarm, incident logging, field dispatch |
| 4 | Emergency shutdown | Recommend initiating the facility ESD procedure |

Table 3. Safety-action space and its alarm boundary. Actions 3 and 4 are alarm-grade: each places a notification in front of an operator. Actions 1 and 2 do not, and every metric in Section 3.5 follows that boundary exactly, counting escalation as a ≥ 3 and under-escalation as a ∈ {1, 2}. The boundary is a modeling choice about this implementation rather than a claim about how a verification request must be handled in general, and moving it would change several results in Sections 4.3 and 4.6.

### 3.3 Component models

Perception. Thermal images are classified with YOLOv8n-cls (Jocher et al. 2023), the smallest classification variant in the family: images resized to 224 by 224, pretrained initialization, AdamW at 10⁻³ with cosine annealing, weight decay 10⁻⁴, batch size 32, 50 epochs, with random flip, rotation and brightness augmentation, on an 80/20 stratified split of the 6,400 frames. That split is randomized over frames captured consecutively within a single session, so it is exposed to the same leakage mechanism the sensor-side holdout was built to avoid. Adjacent thermal frames are close to duplicates. Treat the perception accuracy below as an optimistic upper bound, then, rather than a performance estimate. The image corpus was not available when this revision was prepared, so the split could not be corrected (Appendix A).

Anomaly detection. An LSTM autoencoder with a single-layer encoder and decoder, hidden dimension 32 and a linear output, trained on NoGas windows only, following Malhotra et al. (2016). The mean reconstruction error over the full 20-step window is the anomaly score. The threshold τ is the 95th percentile of reconstruction error on NoGas training windows only, and evaluation is on held-out windows (Section 4.1). That distinction turns out to matter a great deal.

Coordination. The 22-dimensional decision state is

φₜ = [ ρ̃ₜ , Xₜ[−1,:] , δₜ , σₜ ] ∈ ℝ²² ………………………………………….(1)

with ρ̃ₜ the normalized anomaly score, Xₜ[−1,:] the current seven-channel reading, δₜ the per-sensor change across the window, and σₜ the per-sensor standard deviation. There is no visual term in the state. Thermal evidence feeds the perception and explanation paths, not the action.

Decision. A feedforward network with a dueling value and advantage head (Wang et al. 2016), mapping φₜ to five action scores, trained by cost-weighted cross-entropy. Not by reinforcement learning, despite the architecture’s provenance. Target actions come from a deterministic map a*(·) from class to acceptable action set: NoGas to {0}, Smoke to {3}, Mixture to {4}, Perfume to {1, 2}. Each sample carries a loss weight w(gₜ) equal to c_miss for hazardous classes and c_false otherwise, with C = c_miss / c_false. The objective is

L(θ) = − (1/N) Σₜ w(gₜ) · log p_θ( a*(gₜ) | φₜ ) …………………………….(2)

where p_θ is the softmax over action scores. The deployed configuration uses C = 8:1, and Section 4.4 sweeps the rest.

Two consequences of Eq. 2 bound what can honestly be claimed from any of this, and a reader will derive them anyway, so we may as well.

The target action is a deterministic function of the class label. Decision accuracy comes out as four-class classification accuracy composed with a fixed map, not a separate quantity measured on a separate task. What differs between the “decision” framing and the “classification” framing is the error metric, not the task, and the error metric is what this paper is about.

A rule that applies a*(·) to the true label reaches 100% decision accuracy by construction. Such a rule consumes the very label it is supposed to infer, so it is not deployable. Where it appears below we call it a label-function reference, never a baseline. The deployable version of the same idea is the depth-3 threshold rule described next.

Reasoning. Explanations are generated locally with Gemma 3 1B served through Ollama (Google DeepMind 2025), prompted with the gas class, classification confidence, normalized anomaly score and threshold, and the selected action, capped at 150 tokens. Nothing leaves the device. The explanation is advisory and sits off the safety-critical path: the action is fixed by the decision component and the generated text cannot change it. That separation was deliberate, on the reasoning that a fluent explanation inconsistent with the decision is a hazard in a control room rather than an aid. We should be clear that the explanation component is described here as part of the system and is not evaluated anywhere in this paper. No result below depends on it.

### 3.4 Comparators

Eleven comparators, one protocol. The cost-weighted policy of Eq. 2; an unweighted network of identical topology; a multilayer perceptron (256-256-128); cost-sensitive gradient boosting (300 trees); an RBF support-vector classifier; a random forest (300 trees); a recurrent network over K = 10 consecutive states; conservative Q-learning with a TD(0) bootstrap and a conservative penalty on non-behavior actions; k-nearest neighbours with k = 5; a threshold rule, meaning a depth-3 decision tree restricted to the seven raw current-sensor channels, which is interpretable, deployable and about as close to current practice as we could make it; and CUSUM (Page 1954), a one-sided cumulative-sum detector on the anomaly score, with μ₀ and σ estimated from NoGas training windows and the decision threshold set on the training partition. CUSUM is two-class by construction. It emits only Monitor and Raise alarm, so it cannot separate Smoke from Mixture and its decision accuracy is not comparable with the multiclass models. A reader should not take its 0.4994 in Table 5 as evidence that the detector failed; it is an artifact of scoring a two-state output against a four-class target map. Its missed-hazard rate and escalation adequacy are directly comparable, because those definitions do not depend on how many classes a model can express.

Not every comparator appears in every experiment, so the subsets are worth stating plainly. All eleven appear in the in-distribution comparison. The leave-one-class-out grid uses eight: CUSUM is excluded because a two-state output makes its escalation column degenerate by construction, and the recurrent network and conservative Q-learning were not included in that grid. The degradation campaign uses five, fixed before any of its results were seen, spanning one cost-weighted network, one plain feedforward model, two tree ensembles and the interpretable rule. Calibration uses only the cost-weighted policy, because the four estimators being compared are properties of a single model’s confidence rather than of the model inventory, and the ablation likewise holds the architecture fixed so that the feature set is the only thing varying. These are different experiments on overlapping subsets and should not be read across as though they were one. Whether the recurrent and conservative Q-learning comparators ought to be added to the leave-one-class-out grid is a question we leave open (Appendix C).

### 3.5 The metric set

Five quantities rather than one. This set is the methodological proposal.

Decision accuracy. The share of test windows assigned an action in a*(gₜ). Reported for continuity with prior work. It is not a safety metric and we do not treat it as one. Of the five quantities below, missed-hazard rate and escalation adequacy are safety-relevant in the sense that each corresponds to a distinct operational failure; the high-severity false-alarm rate is an alarm-management quantity with safety consequences at sufficient rate; and decision accuracy is neither. We should also be clear that these four together are a proposed subset of what matters operationally, not a definition of safety.

Missed-hazard rate. This is the share of hazardous windows, Smoke and Mixture together, assigned the passive Monitor action. Only a = 0 counts. Assigning a hazardous window to Raise Alarm when Emergency Shutdown was the target is not a miss, because an operator still gets notified. The limitation is that assigning a hazardous window to Increase Sampling or Request Verification is also not a miss, even though nobody is notified. Section 4.3 shows that this is not an academic worry, which is why the next metric exists.

Escalation adequacy. Here we count the share of hazardous windows assigned an alarm-grade action (a ≥ 3), which is what decides whether an operator hears about the hazard. We also report under-escalation, the share receiving a ∈ {1, 2}.

High-severity false-alarm rate. The share of clean windows that gets assigned a ≥ 3. Worth noting that the project’s original evaluation code divided false alarms by the number of alerts rather than the number of clean windows; the two agree only at zero, which is why the discrepancy went unnoticed. Everything here uses the per-clean-window definition. Section 4.6 also expresses it as alarms per 1,000 clean windows, because a bare rate is not comparable with the envelopes an operator actually works inside (EEMUA 2013; ISA 2016).

Bounds on every zero. An observed zero is not a demonstrated zero. All zero-count claims carry a one-sided 95% Clopper-Pearson upper bound (Clopper and Pearson 1934). Pooled across five seeds this study sees 3,160 hazardous and 1,580 clean test windows, so a zero supports “at most 0.095%” and “at most 0.189%” respectively. Getting below 10⁻³ would need something like 2,995 consecutive zero-miss observations, which puts the usual “0.0000” in a table into perspective.

### 3.6 Protocol and statistics

Five seeds (42, 1337, 7, 2024, 99), each with its own block position, determinism guards on, single-threaded execution.

One constraint deserves emphasis because it is easy to trip over. With n = 5 paired seeds the two-sided Wilcoxon signed-rank test has a minimum attainable p-value of 2^(1−n) = 0.0625. No comparison in this design can reach α = 0.05 at any effect size whatsoever. We assert no significance-based ranking as a result, and would ask readers not to infer one. Paired p-values appear in the tables for completeness, with that constraint stated beside them. Getting to a properly powered comparison would take many more randomized runs varying seed, split, augmentation and hyperparameter draw, together with an equivalence analysis over a region of practical equivalence (Benavoli et al. 2017; Bouthillier et al. 2021). We flag it as work still to do rather than pretending otherwise.

## 4. Results

### 4.1 Component behavior

Perception. The thermal classifier reached 98.8% top-1 accuracy on 1,280 held-out validation images (Table 4), with perfect recall for Smoke and Mixture. The 15 misclassifications all sat on the NoGas and Perfume boundary.

| Gas class | Precision | Recall | F1 | Accuracy (%) |
| --- | --- | --- | --- | --- |
| Mixture | 1.000 | 1.000 | 1.000 | 100.0 |
| NoGas | 0.990 | 0.963 | 0.976 | 96.3 |
| Perfume | 0.972 | 0.991 | 0.981 | 99.1 |
| Smoke | 0.991 | 1.000 | 0.995 | 100.0 |
| Overall | 0.988 | 0.988 | 0.988 | 98.8 |

Table 4. Perception component, 1,280 held-out validation images. Obtained under a randomized image split (Section 3.3), so read as an optimistic upper bound.

Fig. 3. Thermal classifier behavior on 1,280 held-out validation images. (a) Counts, (b) row-normalized, (c) per-class scores. All 15 errors fall on the NoGas and Perfume boundary; neither hazardous class is confused with a non-hazardous one, which is what matters once the class label is mapped to an action. The split is randomized over consecutive frames from a single session, so these values should be read as an optimistic bound rather than an independent estimate.

Anomaly detection. Two questions decide how much weight this component can carry, and both are easy to answer wrongly.

Does the score track hazard? Mean reconstruction error by class comes out at NoGas 0.736, Perfume 1.543, Mixture 117.72 and Smoke 229.25 (Fig. 2a). Hazardous conditions separate from benign ones by two orders of magnitude, so the score is usable as a hazard indicator. It is not monotone in target severity, though: Mixture carries the higher target action, Emergency Shutdown, yet scores well below Smoke. The score is best read as evidence of abnormality rather than as a severity estimate, and no result in this paper leans on it being the latter.

Does the partition used to fit the threshold matter? Considerably, and in a way that is worth showing rather than asserting. Setting τ at the 95th percentile of all NoGas windows and then evaluating on those same windows returns AUC 0.962 at a false-positive rate of exactly 5.000%, which is simply the nominal value a 95th-percentile threshold produces on the sample that defined it. That number measures the definition, not the detector. Fitting τ on NoGas training windows only and evaluating on held-out windows gives ROC-AUC 0.9928 ± 0.0053, TPR 0.7363 ± 0.0949 and FPR 0.0000 ± 0.0000 across five seeds (Fig. 2b). Discrimination improves and no false positive is observed, while sensitivity falls by roughly seven points. The held-out figures are the ones we report, and the in-sample pair is shown alongside in Fig. 5a only to make the size of the difference visible.

The zero deserves the same treatment we give every other zero in this paper. No false positive was observed on the held-out NoGas windows; across the five partitions that is 1,580 windows, which bounds the underlying rate at 0.189% with 95% confidence and no lower.

Fig. 4. Anomaly component. (a) Mean reconstruction error by class, log scale. (b) Operating point with the threshold fitted on its own sample, against the threshold fitted on training windows and evaluated on held-out windows.

Fig. 5. Anomaly detector in detail. (a) ROC curves, one per seed for the held-out evaluation, against the in-sample curve, with both operating points marked. (b) Score distributions by class on a log axis. The gap between the benign pair and the hazardous pair is close to two decades, while NoGas and Perfume overlap substantially, which is where the residual errors come from.

### 4.2 In distribution, eleven models look identical

All models trained on the same partition with the same five seeds, evaluated on the same holdout (Table 5, Fig. 3).

| Model | Decision accuracy | SD | Missed-hazard | 95% CP bound | Escalation | High-severity FA | Wilcoxon p vs. cost-weighted |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Random forest | 0.9769 | 0.0086 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.1875 |
| Recurrent (LSTM) | 0.9680 | 0.0231 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.8125 |
| Gradient boosting | 0.9634 | 0.0211 | 0.0098 | ≤ 1.322% | 0.990 | 0.0000 | 1.0000 |
| Cost-weighted policy | 0.9623 | 0.0214 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | reference |
| Multilayer perceptron | 0.9612 | 0.0110 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.8125 |
| Unweighted network | 0.9562 | 0.0386 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 1.0000 |
| k-nearest neighbours | 0.9521 | 0.0295 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.1250 |
| Support vector classifier | 0.9511 | 0.0190 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.4375 |
| Conservative Q-learning | 0.9438 | 0.0485 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.3750 |
| Threshold rule (depth-3) | 0.9297 | 0.0295 | 0.0000 | ≤ 0.095% | 1.000 | 0.0000 | 0.1875 |
| CUSUM (two-class) | 0.4994* | 0.0004 | 0.0013 | ≤ 0.289% | 0.999 | 0.0000 | 0.0625 |

Table 5. Model comparison on the block-wise holdout, five seed-varying partitions. Pooled n = 3,160 hazardous and 1,580 clean test windows. *CUSUM emits only actions 0 and 3, so its decision accuracy is not comparable; its safety columns are. The minimum attainable two-sided p at n = 5 is 0.0625, so nothing in the last column can reach α = 0.05.

Three things stand out.

The ten multiclass models span 4.7 accuracy points, from 0.9297 to 0.9769. Highest point accuracy and lowest variance belong to the random forest. The cost-weighted policy sits fourth. What we did not expect is that the depth-3 threshold rule on seven raw sensor channels lands only 3.3 points behind the best learned model and within one standard deviation of four of them.

More striking, the safety metrics do not discriminate at all in distribution. Ten of eleven models record no observed missed hazards, escalation adequacy of 1.000, and no observed high-severity false alarms. Those zeros are counts, not rates: pooled across seeds they support “at most 0.095%” and “at most 0.189%”, and nothing stronger. Gradient boosting is the lone exception at 0.0098. Taken at face value, a three-level decision tree reproduces the safety behavior of every deep model we tested on this benchmark, which is not the conclusion we set out to reach. We would resist the stronger reading. The result says that a simple rule captures most of the nominal classification structure of this corpus, not that simple models are generally preferable; Sections 4.3 and 4.6 show the same rule failing badly on one unseen hazard and becoming an alarm generator under sensor loss. Its value here is as an interpretable reference point that makes the saturation visible.

And no ranking is asserted, because the design cannot support one. The smallest observed p is 0.0625 (CUSUM), which is the minimum attainable value rather than evidence of anything. What Table 5 supports is the weaker statement that these models are not distinguishable in distribution. That happens to be the premise for everything after it.

Fig. 6. Decision accuracy on the block-wise holdout, mean ± SD across five seed-varying partitions. The shaded band spans the full range of model means.

Looking at where the actions actually land (Fig. 7) makes the saturation concrete. Every model sends essentially all Smoke windows to Raise Alarm and all Mixture windows to Emergency Shutdown, and the only visible spread is on the NoGas and Perfume boundary, where models split between Monitor and Increase sampling in slightly different proportions.

One detail there deserves a mention, since it is a property of the action space rather than of any model. Action 2, Request Verification, is never selected by any model, on any seed. The target map sends Perfume to action 1, so action 2 is never a training target and cannot be scored correct. The five-level ladder is, in practice, a four-level one. Whether action 2 should exist at all, and what condition ought to generate it (high predictive uncertainty would be the obvious candidate), is a design question the current setup never has to answer.

Fig. 7. Action-selection matrices in distribution, averaged over five seeds. Rows are gas classes, columns are actions. The empty Request Verification column is the same in every panel.

### 4.3 Out of distribution, the picture falls apart

Each hazardous class was withheld in turn, models retrained on the remaining three, then evaluated on every window of the withheld class. Feature scaling and anomaly normalization were fitted on the three training classes only, so no statistic of the withheld class leaks into training. (Our first pass fitted the scaler on all four, and we caught it only on a re-read; the numbers below are from the corrected run.) Held-out decision accuracy is zero by construction, since withholding a class removes its target action from the training label set and the model simply cannot emit it. What the model does instead is the interesting part. Table 6 and Figs. 8 to 10 report it.

| Held-out | Model | Missed-hazard | 95% CP bound | Escalation (a ≥ 3) | Under-escalation (a ∈ {1,2}) |
| --- | --- | --- | --- | --- | --- |
| Smoke | Cost-weighted policy | 0.0000 | ≤ 0.038% | 1.000 ± 0.000 | 0.000 |
| Smoke | Gradient boosting | 0.0000 | ≤ 0.038% | 1.000 ± 0.000 | 0.000 |
| Smoke | Random forest | 0.0000 | ≤ 0.038% | 1.000 ± 0.000 | 0.000 |
| Smoke | Threshold rule | 0.0000 | ≤ 0.038% | 1.000 ± 0.000 | 0.000 |
| Smoke | Unweighted network | 0.0001 | ≤ 0.060% | 0.9999 ± 0.0003 | 0.000 |
| Smoke | Support vector classifier | 0.0042 | ≤ 0.558% | 0.928 ± 0.023 | 0.068 |
| Smoke | k-nearest neighbours | 0.0116 | ≤ 1.383% | 0.943 ± 0.005 | 0.045 |
| Smoke | Multilayer perceptron | 0.0949 | ≤ 10.047% | 0.902 ± 0.130 | 0.003 |
| Mixture | Cost-weighted policy | 0.0000 | ≤ 0.038% | 0.226 ± 0.209 | 0.774 |
| Mixture | Gradient boosting | 0.0000 | ≤ 0.038% | 1.000 ± 0.000 | 0.000 |
| Mixture | Random forest | 0.0000 | ≤ 0.038% | 0.990 ± 0.010 | 0.010 |
| Mixture | Support vector classifier | 0.0003 | ≤ 0.080% | 0.005 ± 0.008 | 0.995 |
| Mixture | Unweighted network | 0.0004 | ≤ 0.098% | 0.215 ± 0.215 | 0.785 |
| Mixture | Multilayer perceptron | 0.0070 | ≤ 0.870% | 0.242 ± 0.121 | 0.751 |
| Mixture | k-nearest neighbours | 0.0254 | ≤ 2.854% | 0.205 ± 0.072 | 0.770 |
| Mixture | Threshold rule | 0.2487 | ≤ 25.683% | 0.564 ± 0.399 | 0.188 |

Table 6. Leave-one-class-out evaluation. n = 1,581 windows per class per seed; bounds pooled over 7,905 evaluations. Scaling fitted on the three training classes only.

In-distribution accuracy does not order out-of-distribution missed-hazard rate. On withheld Smoke the multilayer perceptron, which sat fifth of ten by point accuracy in Table 5 and was statistically indistinguishable from everything else there, assigns the passive Monitor action to 9.49% of unseen hazardous windows, with a 95% bound of 10.05%. Four other models are bounded at 0.038%. That is a separation of more than two orders of magnitude, entirely invisible in Table 5, and the rank correlation between the two is close to nil (Pearson r = +0.12 for missed hazard on unseen Smoke, r = +0.36 for escalation on unseen Mixture, Fig. 8). No accuracy-based selection procedure would have steered a team away from the failing model.

Fig. 8. In-distribution accuracy against out-of-distribution safety. Each point is one model. If accuracy carried information about safety behavior these panels would show a trend, and they do not.

Missed-hazard rate is not enough on its own, and this is the sharper of the two results. On withheld Mixture, seven of eight models are bounded below 2.9% on missed hazards and would pass any review conducted on that number. Their escalation adequacy runs from 0.5% to 100%, a factor of about 198. The support-vector classifier misses 0.03% of unseen hazardous windows while escalating 0.5% of them, which means it answers roughly 99.5% of the most hazardous class in the corpus with Increase Sampling or Request Verification. The miss metric records that as a clean sheet. The cost-weighted policy escalates 22.6% and under-escalates 77.4%. Gradient boosting, carrying none of the pipeline’s safety machinery, escalates all of them.

Which metric you pick, rather than which model you pick, is what decides whether a model looks safe. A metric set reporting missed-hazard rate alone would rank the support-vector classifier above gradient boosting on this evidence, and would be wrong by a factor of 198 on the quantity that decides whether anyone is notified.

Worth noting as well: the two models that escalate fully on both unseen hazards are tree ensembles, and the deployable threshold rule fails safe on unseen Smoke while failing badly on unseen Mixture at 24.87% (bound 25.68%). No comparator is uniformly best. That is itself an argument for reporting the full set rather than picking a favourite metric and defending it.

Fig. 9. Behavior on a hazardous class withheld from training, eight comparators, mean over five seed-varying partitions. (a) Missed-hazard rate, drawn on a logarithmic axis because the values span three decades and a linear axis renders a 9.49% failure and a 0.03% one at visually indistinguishable heights. Bars at the floor line are observed zeros, bounded at 0.038%. (b) Escalation adequacy with ± 1 SD across seeds. The two panels disagree about which models are acceptable, which is the point of showing them together.

Fig. 10. Where hazardous windows actually go. Each bar decomposes the response to an unseen hazardous class into alarm-grade, sub-alarm and passive. The support-vector column under held-out Mixture is almost entirely sub-alarm, and its missed-hazard rate is 0.0003.

### 4.4 Cost asymmetry moves accuracy and nothing else

The loss-weight ratio C from Eq. 2 was swept across nine values with everything else fixed (Table 7, Fig. 11).

| Cost ratio C | Decision accuracy | SD | Missed-hazard | Escalation | High-severity FA |
| --- | --- | --- | --- | --- | --- |
| 1:1 (symmetric) | 0.9562 | 0.0386 | 0.0000 | 1.000 | 0.0000 |
| 2:1 | 0.9532 | 0.0418 | 0.0000 | 1.000 | 0.0000 |
| 4:1 | 0.9570 | 0.0390 | 0.0000 | 1.000 | 0.0000 |
| 6:1 | 0.9655 | 0.0272 | 0.0000 | 1.000 | 0.0000 |
| 8:1 (deployed) | 0.9623 | 0.0214 | 0.0000 | 1.000 | 0.0000 |
| 10:1 | 0.9589 | 0.0338 | 0.0000 | 1.000 | 0.0000 |
| 12:1 | 0.9533 | 0.0346 | 0.0000 | 1.000 | 0.0000 |
| 16:1 | 0.9427 | 0.0463 | 0.0000 | 1.000 | 0.0000 |
| 20:1 | 0.8389 | 0.1189 | 0.0000 | 1.000 | 0.0000 |
| Label function | 1.0000 | 0.0000 | 0.0000 | 1.000 | 0.0000 |

Table 7. Cost-asymmetry sweep, five seeds per configuration. The label-function row applies a*(·) to the true class label. It reaches the ceiling by construction, consumes the label it is meant to infer, and is not a deployable baseline.

Missed-hazard rate is zero and escalation adequacy is 1.000 at every ratio, the symmetric 1:1 configuration included. Accuracy climbs to a maximum of 0.9655 at 6:1, sits at 0.9623 at the deployed 8:1, then falls away to 0.8389 at 20:1, twelve points below the peak with variance up roughly fourfold.

So the asymmetry produced no measurable safety benefit here and, past 6:1, cost accuracy. The reason looks structural rather than accidental. Because the target action is a deterministic function of a well-separated class label, and because a miss under this definition requires assigning a hazardous window to the class furthest from it in feature space, the miss rate is already sitting on the floor before any weighting is applied. There is nothing for the asymmetry to reshape.

We would not read that as evidence against cost-sensitive learning in general. The literature is clear that it works where the error surface is non-trivial (Elkan 2001). What this benchmark shows is that it cannot demonstrate the effect, and by extension that no saturated, well-separated benchmark can. Validating a safety objective seems to need either a corpus where hazardous and benign states genuinely overlap, or a metric under which sub-alarm responses carry cost. Section 4.3 supplies the second, and under it the cost-weighted policy is not the leader.

One more thing about the deployed configuration. C = 8:1 is not the accuracy optimum, and it was originally chosen on test-partition dispersion, which is not a defensible selection criterion. Re-selecting on a validation split is on the list in Appendix A.

Fig. 11. Cost-asymmetry sweep. Shading is ± 1 SD across five seed-varying partitions.

### 4.5 What the decision state actually contributes

The decision state was ablated by feature group with the architecture and protocol held fixed (Table 8, Fig. 12).

| Decision state | d | Decision accuracy | SD | Δ vs. full | Missed-hazard | Escalation |
| --- | --- | --- | --- | --- | --- | --- |
| Full state | 22 | 0.9612 | 0.0110 | reference | 0.0000 | 1.000 |
| Without per-sensor σ | 15 | 0.9601 | 0.0357 | −0.11 pp | 0.0000 | 1.000 |
| Without anomaly score | 21 | 0.9574 | 0.0206 | −0.38 pp | 0.0000 | 1.000 |
| Without per-sensor δ | 15 | 0.9399 | 0.0413 | −2.14 pp | 0.0000 | 1.000 |
| Without δ and σ | 8 | 0.8875 | 0.0730 | −7.37 pp | 0.0000 | 1.000 |
| Current readings only | 7 | 0.8845 | 0.0764 | −7.67 pp | 0.0000 | 1.000 |
| Anomaly score only | 1 | 0.7513 | 0.1349 | −21.00 pp | 0.0000 | 1.000 |

Table 8. Decision-state ablation, five seeds.

Temporal features carry the accuracy. Dropping both δ and σ costs 7.37 points, and a single anomaly score on its own still manages 75.1%, which surprised us. But missed-hazard rate stays at zero and escalation adequacy stays at 1.000 in every condition, including the one-dimensional state. No feature group in this decision state changes in-distribution safety behavior at all.

That is another instance of the same trap. An ablation reported on accuracy alone would seem to identify which features “drive safety behavior,” and it would be measuring something else entirely.

Fig. 12. Decision-state ablation. Bars are mean ± SD decision accuracy. Missed-hazard rate and escalation adequacy are constant across every condition.

Retraining without a feature answers whether the feature is necessary. A sharper question, and the one that matters if an upstream component can fail in service, is what a trained model does when that input goes wrong while everything else stays correct. We swept the anomaly score across its full range on every test window, holding the other twenty-one features fixed, and recorded how often the selected action moved (Fig. 13).

The models divide sharply. For the threshold rule the answer is zero by construction, since it reads only the seven raw channels. For k-nearest neighbors, the support-vector classifier and the multilayer perceptron the action moves on under 4% of windows; for the cost-weighted policy on 8.0 ± 5.8% and for the random forest on 16.1 ± 7.6%. Gradient boosting is the outlier at 60.6 ± 7.9%. Whatever the anomaly channel contributes to the other models, it is close to inert at inference time; for gradient boosting it is load-bearing.

The consequence shows up in the safety metrics, and only for that one model. Forcing the anomaly score to zero, which is what a failed or unconnected autoencoder would supply, leaves the missed-hazard rate of every other comparator at zero and moves gradient boosting from 0.0098 to 0.3405, with escalation adequacy falling from 0.990 to 0.495. A model that looked mid-table in Table 5 turns out to have its safety behavior resting on a single upstream input, and nothing in the accuracy column or the ablation table shows it.

We would not over-read a single conditional probe. The override is synthetic, the other features are held at values that in reality would co-vary with the anomaly score, and one corpus is a narrow basis for a claim about any model family. Still, the finding is consistent with two results we already had: gradient boosting is the model that fails silent under sensor loss (Section 4.6) and the one that escalates unseen Mixture perfectly while others do not (Section 4.3). A heavier dependence on the anomaly channel is a plausible common mechanism for all three, and it suggests that dependence on upstream components deserves to be measured rather than assumed, particularly where those components can fail independently of the model consuming them.

Fig. 13. Dependence of the selected action on the anomaly input, five seed-varying partitions. (a) Share of test windows whose action changes at any point as the anomaly score is swept across [0, 1] with all other features held fixed, mean ± 1 SD. (b) Missed-hazard rate against the forced anomaly value. Six comparators are flat; gradient boosting moves from 0.0098 to 0.3405 when the channel reads zero.

### 4.6 Under degradation, three distinct failure modes

Six models were put through additive noise (σ = 0.1 to 0.5), calibration drift (gain and baseline shift of ±10% to ±50%) and channel dropout (k = 1 to 7 of 7 sensors), each at graded severity, with all three safety metrics reported (Table 9, Figs. 14 and 15).

| Condition | Model | Decision acc. | Missed-hazard | Escalation | High-severity FA | Alarms per 1,000 windows |
| --- | --- | --- | --- | --- | --- | --- |
| Clean | Cost-weighted | 0.962 | 0.0000 | 1.000 | 0.0000 | ≤ 1.9* |
| Clean | Random forest | 0.977 | 0.0000 | 1.000 | 0.0000 | ≤ 1.9* |
| Clean | Threshold rule | 0.930 | 0.0000 | 1.000 | 0.0000 | ≤ 1.9* |
| Drift ±50% | Cost-weighted | 0.916 | 0.0000 | 1.000 | 0.0006 | 0.6 |
| Drift ±50% | Multilayer perceptron | 0.927 | 0.0003 | 0.999 | 0.0000 | 0 |
| Drift ±50% | Gradient boosting | 0.876 | 0.0775 | 0.890 | 0.0000 | 0 |
| Noise σ = 0.5 | Cost-weighted | 0.843 | 0.0000 | 1.000 | 0.1342 | 134 |
| Noise σ = 0.5 | Random forest | 0.889 | 0.0000 | 1.000 | 0.0063 | 6.3 |
| Dropout k = 1 | Cost-weighted | 0.883 | 0.0000 | 1.000 | 0.1171 | 117 |
| Dropout k = 1 | Threshold rule | 0.723 | 0.0000 | 1.000 | 0.2000 | 200 |
| Dropout k = 1 | Random forest | 0.974 | 0.0000 | 1.000 | 0.0000 | 0 |
| Dropout k = 3 | Cost-weighted | 0.793 | 0.0000 | 0.992 | 0.1532 | 153 |
| Dropout k = 3 | Multilayer perceptron | 0.851 | 0.0218 | 0.975 | 0.0234 | 23 |
| Dropout k = 7 | Cost-weighted | 0.318 | 0.0000 | 1.000 | 1.0000 | 1,000 |
| Dropout k = 7 | Threshold rule | 0.250 | 0.0000 | 1.000 | 1.0000 | 1,000 |
| Dropout k = 7 | Random forest | 0.355 | 0.0000 | 1.000 | 0.6000 | 600 |
| Dropout k = 7 | Multilayer perceptron | 0.332 | 0.5266 | 0.473 | 0.2000 | 200 |
| Dropout k = 7 | Gradient boosting | 0.381 | 0.6000 | 0.400 | 0.0000 | 0 |

Table 9. Selected perturbation results, with the full sweep in Fig. 14. Alarm burden is the high-severity false-alarm rate expressed per 1,000 clean windows, per detector, which keeps it independent of any particular duty cycle. *The clean-condition burden is the Clopper-Pearson upper bound on an observed zero, not a point estimate.

Three failure modes separate cleanly, and no single metric tells them apart.

Fail-loud. The cost-weighted policy and the threshold rule record no observed missed hazards and full escalation right through complete sensor loss, and they do it by escalating everything. False-alarm rate reaches 1.000, meaning every clean window raises a high-severity alarm. Under EEMUA (2013) that is a hazard, not a safe failure. On the missed-hazard metric alone it is a perfect score.

Fail-silent. Gradient boosting records no false alarm at any severity and misses 60% of hazards at k = 7, escalation collapsing to 0.400. On the false-alarm metric alone, also a perfect score.

Graceful, then brittle. The random forest holds zero misses, full escalation and no false alarms out to k = 3, then jumps to a 60% false-alarm rate by k = 7.

The number that matters operationally is the first onset rather than the endpoint. Losing one sensor of seven takes the cost-weighted policy from zero to 117 high-severity alarms per 1,000 clean windows, and the threshold rule to 200, while the random forest is unaffected (Fig. 15).

Converting a rate into a burden is worth spelling out, because a bare rate is hard to place against the envelopes an operator works inside, whereas an alarm count is not. The complication is that any count per unit time needs a duty cycle, and the corpus as distributed carries no timestamp column, so we cannot establish the acquisition interval from the data itself. We therefore report alarms per 1,000 clean windows as the primary quantity and treat any hourly figure as an illustrative scenario rather than a property of a detector. As an illustration only: a detector processing one window every 2 s would see about 1,800 windows per hour, which would put the single-sensor-loss figure near 211 alarms per hour from one instrument. EEMUA (2013) treats something in the region of six alarms per hour as the upper limit of what an entire operator position can absorb. We would not press that comparison further. Model-generated indications are not the same object as a complete plant alarm system, and the conversion assumes a duty cycle we did not measure. What survives without any of those assumptions is the ordering and the magnitude: neither an accuracy table nor a missed-hazard table would have predicted that one lost channel separates these models by two orders of magnitude in alarm production.

The same arithmetic cuts the other way on the clean-condition rows, which is easy to miss. Every model records zero high-severity false alarms on clean data, and that sounds conclusive until the Clopper-Pearson bound is converted too. A zero across 1,580 clean windows supports only “at most 1.9 alarms per 1,000 windows”, which under the same illustrative duty cycle would be roughly 3.4 per hour, already over half the EEMUA figure for an entire operator position. “Zero false alarms” is not yet evidence of an acceptable alarm load. Getting there needs observation counts one to two orders of magnitude beyond anything reported here.

We should add that below roughly 60% accuracy none of these models is doing the job in any useful sense. “Zero missed hazards” at 31.8% accuracy is a statement about how a model fails, not about whether it is fit for service.

Fig. 14. Graded perturbation suite. Rows share a scale so the panels can be compared. Peak false-alarm rate under drift is 0.06%.

Fig. 15. False-alarm rate expressed as alarm burden, per 1,000 clean windows so the quantity does not depend on a duty cycle. The dashed line marks the EEMUA 191 long-term average envelope for a whole operator position, placed at its equivalent for one window every 2 s. Two models cross it as soon as a single sensor is lost, and three more cross it by the time three are gone.

### 4.7 Calibration

Confidence matters here because any escalation threshold, and any deferral rule, would be set against it. Four estimators were compared on the corrected pipeline: the raw softmax, MC dropout with 20 passes, temperature scaling, and a five-member deep ensemble built from the same model class and objective as the single model rather than from a different one. Temperature is fitted on a calibration split carved out of training, never on the training logits themselves, and ECE uses equal-mass bins because confidence on this corpus piles up near 1 and equal-width bins leave most of the range empty (Table 10, Fig. 16).

| Estimator | ECE | SD | Bootstrap 95% CI | ECE on hazardous windows | Brier | NLL | Accuracy |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Deep ensemble (5) | 0.0162 | 0.0129 | 0.0107 to 0.0253 | 0.0002 | 0.0552 | 0.1082 | 0.9663 |
| MC dropout (20) | 0.0222 | 0.0184 | 0.0150 to 0.0320 | 0.0002 | 0.0613 | 0.1145 | 0.9619 |
| Raw softmax | 0.0244 | 0.0187 | 0.0166 to 0.0342 | 0.0002 | 0.0628 | 0.1397 | 0.9628 |
| Temperature scaling | 0.0263 | 0.0194 | 0.0178 to 0.0358 | 0.0000 | 0.0640 | 0.1560 | 0.9628 |

Table 10. Calibration, five seeds. ECE with 15 equal-mass bins; intervals from 400 bootstrap resamples per seed.

The ensemble comes out lowest and every bootstrap interval overlaps every other, so we would not rank the four with any confidence. Two observations seem more useful than the ordering.

The first is that overall ECE is driven entirely by the non-hazardous classes. Restricted to Smoke and Mixture windows, every estimator is calibrated to within 0.02%, and temperature scaling to within rounding. The miscalibration lives on the NoGas and Perfume boundary, which is the same place the perception errors and the anomaly-score overlap live. For a system whose escalation threshold would be set on hazardous-class confidence, that is reassuring, and it is invisible in a single pooled ECE number.

The second is that temperature scaling made things slightly worse, which is not what the usual account predicts. The fitted temperature is consistently below 1, at 0.839 ± 0.044 across seeds and never above 0.89, meaning the network is under-confident rather than over-confident on this corpus. Sharpening an already under-confident distribution moves it away from calibration. We suspect the cost weighting rather than the architecture is responsible, though we did not test that directly and would not present it as more than a hypothesis. One methodological point does follow with more confidence. Temperature must be fitted on a partition the network has not memorized; fitting it on training logits produces a temperature above 1 and an apparent improvement that does not transfer, which is a plausible way for this estimator to be over-credited elsewhere. The bin-count sweep in Fig. 16c shows the ordering is stable from 5 to 30 bins, so the result is at least not an artifact of the binning choice.

Fig. 16. Calibration. (a) ECE with bootstrap intervals. (b) The same, split into all windows against hazardous windows only. (c) Sensitivity to the number of bins.

### 4.8 Standing relative to prior work on this corpus

Published classification accuracies on MultimodalGasData run from 93% to 99.7%, and the decision accuracies here sit below most of them. We would rather say that plainly than let a reviewer discover it, because the comparison is not like-for-like in either direction and both directions matter.

Against us: our evaluation uses a block-wise holdout with an explicit embargo, discards boundary-straddling windows, moves the partition with the seed, and fits all scaling on the training partition. The published comparisons appear to use randomized splits over overlapping windows from a single recording session, which is the protocol Dennler et al. (2022) showed conflates recording time with class identity. The figures are not directly comparable, and the direction of the bias is known even if its size on this particular corpus is not.

In our favour: the quantities differ. A classification error and an action error do not carry the same operational weight. Confusing two hazardous classes preserves the need to escalate; assigning a hazardous window to Monitor gives up the intervention window. For a like-for-like recognition comparison the relevant number is the thermal classifier’s 98.8%, subject to the split caveat in Section 3.3.

Either way, we are not claiming an accuracy advantage and nothing in the contribution rests on one.

## 5. Discussion

### 5.1 The dissociation, and where its boundary sits

The central result is a dissociation with a fairly sharp edge to it. In distribution, ten model families spanning tree ensembles, kernel methods, feedforward and recurrent networks, offline reinforcement learning and a three-level decision tree are indistinguishable on every metric we report. Not just accuracy: 4.7 points separate best from worst, which this design cannot resolve, and all but one record no observed missed hazards, full escalation and no observed false alarms. A facility choosing among them on in-distribution evidence has no basis for choosing at all, including no basis for preferring a deep model to a decision tree.

Out of distribution the same models separate by more than two orders of magnitude on missed-hazard rate and by roughly 198 times on escalation adequacy, and the orderings do not carry across. The model that fails safe on one unseen hazard under-escalates on another. The two that escalate fully on both are tree ensembles carrying none of the pipeline’s safety machinery. The deployable threshold rule is perfect on one unseen hazard and among the worst on the other.

For practice the implication is direct enough. A team selecting a gas-monitoring model on benchmark accuracy, which is what the published literature on this corpus encourages, gets no information about how the chosen model will behave on a release it has not seen. That is the condition the model will eventually face, and on this evidence it is the only condition in which these models differ at all.

There is a counter-reading worth taking seriously. One could argue that LOCO is an unfairly severe test, since no fielded system is asked to classify a gas absent from its training set, and that the in-distribution agreement is the operationally relevant finding. We are not persuaded, mostly because a MOX array in a facility meets cross-sensitivities and interferent mixtures that were not in anyone’s training set fairly routinely. But the objection is reasonable, and a reader who takes it seriously would draw a narrower conclusion from our results than we do.

### 5.2 Why missed-hazard rate is not enough

Having established that accuracy is the wrong metric, the obvious substitute is missed-hazard rate. Our LOCO results suggest that substitution is insufficient in a specific way.

A miss metric that counts only the fully passive response scores a hazardous window answered with Request Verification as a success. On withheld Mixture, seven of eight models satisfy that metric, all bounded below 2.9% at 95% confidence, while escalating anywhere from 0.5% to 100% of the same windows. An operator running the support-vector configuration would hear nothing for about 99.5% of windows of the most hazardous class in the corpus, and the safety metric would report a clean run.

This looks to us like the most transferable finding here, and it is not specific to gas monitoring. Wherever a graded response hierarchy is learned, a metric defined on the most extreme failure can be satisfied by systematic under-response one rung above it. The fix is to define the metric at the operationally meaningful threshold, which here is whether an operator gets notified, rather than at the worst conceivable outcome.

Section 4.6 shows the mirror-image trap just as clearly. Under complete sensor loss the cost-weighted policy and the threshold rule score perfectly on missed hazard and escalation by escalating everything, raising a high-severity alarm on every clean window. Gradient boosting scores perfectly on false alarms by missing 60% of hazards. Each of the three metrics, taken alone, certifies a different model as safe. Only together do they describe what the system is actually doing.

### 5.3 What the cost asymmetry did, and what it did not

The sweep returns no effect on missed-hazard rate or escalation adequacy at any ratio from 1:1 to 20:1, with an accuracy penalty above 6:1. That is worth sitting with rather than setting aside, because the asymmetric objective was the mechanism by which the pipeline was supposed to be safe.

The explanation appears structural, and it generalizes: on a saturated, well-separated benchmark a safety objective cannot really be validated, because the unsafe behavior it exists to suppress does not occur in the first place. Showing that a cost asymmetry works needs either a corpus where hazardous and benign states genuinely overlap, or a metric under which sub-alarm responses carry cost. Section 4.3 supplies the second, and there the cost-weighted policy escalates 22.6% of unseen Mixture windows against gradient boosting’s 100%.

A fair question at this point is what the learned policy contributes at all. On this evidence, in nominal conditions, nothing a depth-3 decision tree does not contribute, at 3.3 fewer accuracy points and identical safety behavior. Its advantages are narrow and specific: full escalation on unseen Smoke where the perceptron misses 9.49%, and no observed missed hazard under 50% calibration drift where gradient boosting misses 7.75%. Each of those is bought with a false-alarm cost under sensor loss that the tree ensembles do not pay. We would rather present it that way than as a general improvement.

There is a further point about the objective itself that we think matters more than the sweep. Eq. 2 weights samples by class hazard but treats all incorrect actions identically. Under-escalating a hazardous window to Request Verification and over-escalating it to Emergency Shutdown incur exactly the same loss. That is not a cost asymmetry in the sense the safety argument needs, and it is the most plausible mechanical explanation we have for the escalation behavior in Section 4.3. An ordinal objective, or a full cost matrix in which both distance and direction along the action ladder carry cost, is the design the evidence points toward. We have not tested it, and it would be the first thing we would try next.

### 5.4 What this means for deployment

Three conclusions held across every configuration, and they are probably the most portable engineering content here.

Language models belong outside the decision path. That is a safety argument rather than an empirical one: a model whose output cannot be verified against the decision it describes should not be able to change that decision, however fast it runs. We have not measured whether the explanation component would meet any particular timing budget, and nothing here should be read as evidence that it would.

Sensor-loss behavior is an alarm-management decision rather than a modeling one. Losing one sensor of seven moved the cost-weighted policy from zero to 117 high-severity alarms per 1,000 clean windows and left the random forest at zero. Whether that is tolerable is a judgment about operator load, and it cannot be made from an accuracy table.

Qualification has to include sensor loss. Single-channel dropout is the most likely fault a fixed detector will actually experience, and it separates models that look identical on every clean-condition metric. Any acceptance test built only on clean data would pass all of them.

### 5.5 What we are not claiming

None of this establishes that the pipeline detects hydrocarbons, since the corpus contains none. None of it establishes that any model here is fit for service: the largest observation count supporting any zero-count claim is 7,905 evaluations, which bounds a miss rate at 0.038% and no lower. Nothing here validates the coordination and explanation components, which are apparatus, are not experimentally isolated, and support no result we report. And the models are not ranked, because the design cannot rank them.

What the study does support is narrower and, we think, more useful: the evaluation conventions of this literature are not fit for the purpose the literature claims for them, and a metric set costing a few extra columns per experiment reverses model-selection decisions on this corpus.

## 6. Limitations and Threats to Validity

Analyte validity. Incense smoke, alcohol-based vapor and a mixture of the two. These are surrogates. Nothing here establishes detection performance for methane or heavier hydrocarbons, and external validity to petroleum facility monitoring is argued from the shared MOX transduction mechanism rather than shown.

Single session, single device. All 6,400 samples come from one acquisition session on one device. Sensor ageing, device-to-device variability, seasonal ambient swings, wind, hydraulic transients and long-term drift are all absent. Cross-session and cross-device validation is the most important experiment still outstanding.

Statistical power. Five paired seeds cannot resolve differences at α = 0.05 under a Wilcoxon signed-rank test whose minimum attainable two-sided p at n = 5 is 0.0625. No ranking among the models is asserted, and none should be read in.

Metric scope. Missed-hazard rate counts only the fully passive action, which is why escalation adequacy is reported beside it. A graded expected-cost formulation over a full action-distance cost matrix would be better, and we did not attempt one.

Perception split. The thermal-image split is randomized over consecutive frames from one session, so it is exposed to the leakage mechanism the sensor-side protocol excludes. The image corpus was unavailable when this revision was prepared, so it could not be corrected. 98.8% is an optimistic upper bound and no conclusion here rests on it.

Anomaly severity ordering. The anomaly score separates hazardous from benign conditions by two orders of magnitude but is not monotone in target severity, since Mixture scores below Smoke. Read it as evidence of abnormality only.

The anomaly-input probe is a conditional intervention. Section 4.5 forces the anomaly feature to fixed values while the other twenty-one are held at their observed values. In service those quantities co-vary, so the probe isolates a dependence rather than reproducing a realistic failure. It shows that one model’s safety behavior is sensitive to a single upstream input; it does not establish how that input would fail, or how often.

No hardware evaluation. Nothing here establishes that the pipeline runs inside any particular latency, memory or power budget, because no deployment was carried out. Claims about on-device feasibility would need a hardware campaign this study does not have, and the explanation component in particular is described but never timed or evaluated.

Modality scope. The action policy consumes sensor dynamics and the anomaly score only. Visual evidence informs the perception and explanation paths, not the action.

Coordination and explanation layers. The components that coordinate, critique and supervise the pipeline, and the language model that writes the operator-facing explanation, are apparatus. None of them is experimentally isolated and no claim in this paper depends on any of them.

Perturbation realism. Drift is modeled as a per-channel gain and baseline shift applied at test time, and dropout as channel zeroing. Neither reproduces the temporal character of real MOX ageing, and a reviewer would be right to treat the drift results as indicative rather than predictive.

## 7. Conclusions

We evaluated a gas-monitoring pipeline against a broader metric set than accuracy alone, on a public MOX benchmark of laboratory surrogates, under a leakage-controlled block-wise holdout with seed-varying partitions.

- In distribution the metric set does not discriminate. Ten multiclass models spanning very different inductive biases lie within 4.7 accuracy points, and all but one record no observed missed hazards, escalation adequacy of 1.000 and no observed high-severity false alarms, each bounded by the sample size rather than demonstrated to be zero. A depth-3 decision tree on seven raw sensor channels matches every learned model on all three safety metrics.

- Out of distribution, accuracy ranking carries almost no information about safety. Withholding one hazardous class separates the same models by more than two orders of magnitude on missed-hazard rate, 9.49% against a 0.038% bound, with a correlation to in-distribution accuracy of r = +0.12.

- Missed-hazard rate is necessary and not sufficient. On a second unseen hazardous class, seven of eight models are bounded below 2.9% on missed hazards while escalating between 0.5% and 100% of the same windows, a factor of about 198 on the quantity that decides whether an operator is notified, and invisible to a miss metric that counts only the passive action.

- A cost-asymmetric objective produced no measurable safety benefit at any ratio from 1:1 to 20:1, and degraded accuracy above 6:1. Where hazardous and benign states are well separated and the target action is a deterministic function of the class, there appears to be no error surface for a safety objective to reshape.

- Under graded sensor loss three distinct failure modes appear, and each single metric certifies a different model as safe. Fail-loud models raise a high-severity alarm on every clean window while recording no observed missed hazard at all. Fail-silent models record no false alarm at all while missing 60% of hazards. Losing one sensor of seven moves the cost-weighted policy from zero to 117 alarms per 1,000 clean windows and leaves the random forest untouched.

Put together, these results argue for reporting missed-hazard rate with a confidence bound, escalation adequacy, false-alarm burden in alarm-management units, and the degradation of all three under graded sensor loss and drift, alongside accuracy rather than instead of it. On the evidence here an evaluation reporting accuracy alone would have said nothing useful about any of these behaviors, and each safety metric taken on its own would have picked a different model.

Where we would go next, roughly in order: cross-session and cross-device validation; evaluation on a corpus containing a controlled hydrocarbon release; an ordinal or cost-matrix objective that prices under-escalation and over-escalation differently; class-conditional conformal prediction (Angelopoulos and Bates 2023) to turn observed zero-miss counts into distribution-free coverage guarantees on the hazardous class; a properly powered comparison over many randomized runs with an equivalence analysis (Benavoli et al. 2017; Bouthillier et al. 2021); and a systematic treatment of upstream-component failure, since Section 4.5 shows at least one comparator whose missed-hazard rate moves by a factor of thirty-five when a single input is wrong, and we tested only one such input.

## Nomenclature

| Symbol | Definition |
| --- | --- |
| a | safety action, a ∈ {0, 1, 2, 3, 4} |
| a*(·) | acceptable target-action map from gas class to action set |
| C | cost ratio, C = c_miss / c_false |
| c_miss, c_false | loss weights for hazardous and non-hazardous training samples |
| Eₜ | operator-facing explanation at cycle t |
| G | embargo length between training and test partitions, in windows |
| gₜ | ground-truth gas class for window t |
| h | CUSUM decision threshold |
| Iₜ | thermal image at cycle t |
| k | number of sensor channels removed (dropout severity) |
| L(θ) | cost-weighted cross-entropy objective, Eq. 2 |
| N | number of training samples |
| n | number of observations or paired runs |
| p_θ | action probability distribution under parameters θ |
| Sₜ | CUSUM statistic at step t |
| Xₜ | seven-channel sensor window, Xₜ ∈ ℝ^(20×7) |
| δₜ | per-sensor change across the window |
| θ | model parameters |
| μ₀ | CUSUM baseline mean, estimated on NoGas training windows |
| ρ̃ₜ | normalized reconstruction-error anomaly score |
| σₜ | per-sensor standard deviation across the window |
| σ | additive-noise standard deviation (Section 4.6) |
| τ | anomaly detection threshold |
| φₜ | 22-dimensional decision state, Eq. 1 |

Subscript. t, inference cycle or window index.

Abbreviations. CP, Clopper-Pearson; ECE, expected calibration error; ESD, emergency shutdown; FA, false alarm; LOCO, leave-one-class-out; MOX, metal-oxide semiconductor; ROC-AUC, area under the receiver operating characteristic curve; SD, standard deviation; SIS, safety instrumented system; VOC, volatile organic compound.

## Acknowledgments

This work was supported by the Subsurface Energy and Digital Innovation Center (SEDI) at the University of Wyoming. The MultimodalGasData corpus is used under CC BY 4.0, and we thank Narkhede et al. for putting it in the public domain.

## Author Contributions

B. C. Nweke: conceptualization, methodology, software, investigation, formal analysis, data curation, visualization, writing of the original draft. G. Ramezan: conceptualization, methodology, writing, review and editing. S. Saraji: conceptualization, supervision, project administration, resources, writing, review and editing.

## Declaration of Competing Interest

The authors declare no known competing financial interests or personal relationships that could have appeared to influence the work reported here.

## Data and Code Availability

The MultimodalGasData corpus is publicly available (Narkhede et al. 2022) under CC BY 4.0. Experiment drivers, the safety-metric module, the additional baselines, model checkpoints and the result files behind Tables 5 to 10 are available from the corresponding author. See Appendix B.

## References

Adegboye, M. A., Fung, W. K., and Karnik, A. 2019. Recent Advances in Pipeline Monitoring and Oil Leakage Detection Technologies: Principles and Approaches. Sensors 19 (11): 2548. https://doi.org/10.3390/s19112548.

Angelopoulos, A. N. and Bates, S. 2023. Conformal Prediction: A Gentle Introduction. Foundations and Trends in Machine Learning 16 (4): 494–591. [CITATION NEEDED, verify volume and pagination]

Benavoli, A., Corani, G., Demšar, J. et al. 2017. Time for a Change: A Tutorial for Comparing Multiple Classifiers Through Bayesian Analysis. Journal of Machine Learning Research 18 (77): 1–36.

Bouthillier, X., Delaunay, P., Bronzi, M. et al. 2021. Accounting for Variance in Machine Learning Benchmarks. Proc., Machine Learning and Systems (MLSys) 3: 747–769. [CITATION NEEDED, verify pagination]

Bustnes, T. E., Rousselet, M., and Berland, S. 2011. Leak Detection Performance of a Commercial Real-Time Transient Model. Paper presented at the PSIG Annual Meeting, Napa Valley, California, 24–27 May. PSIG-1114.

Clopper, C. J. and Pearson, E. S. 1934. The Use of Confidence or Fiducial Limits Illustrated in the Case of the Binomial. Biometrika 26 (4): 404–413. https://doi.org/10.1093/biomet/26.4.404.

Dehnaw, A. M., Manie, Y. C., Yao, C.-K. et al. 2024. Deep Neural Network Optimization for Efficient Gas Detection Systems in Edge Intelligence Environments. Processes 12 (12): 2638. [CITATION NEEDED, verify author list and issue]

Dennler, N., Rastogi, S., Fonollosa, J. et al. 2022. Drift in a Popular Metal Oxide Sensor Dataset Reveals Limitations for Gas Classification Benchmarks. Sensors and Actuators B: Chemical 361: 131668. [CITATION NEEDED, verify volume and article number]

EEMUA. 2013. Alarm Systems: A Guide to Design, Management and Procurement, third edition. EEMUA Publication 191. London: Engineering Equipment and Materials Users Association.

El Barkani, M., Benamar, N., Talei, H. et al. 2024. Gas Leakage Detection Using Tiny Machine Learning. Electronics 13 (23): 4768. https://doi.org/10.3390/electronics13234768.

Elkan, C. 2001. The Foundations of Cost-Sensitive Learning. Proc., 17th International Joint Conference on Artificial Intelligence (IJCAI), Seattle, Washington, 4–10 August, 973–978.

Faleh, R. and Kachouri, A. 2023. A Hybrid Deep Convolutional Neural Network-Based Electronic Nose for Pollution Detection. Chemometrics and Intelligent Laboratory Systems 237: 104825. https://doi.org/10.1016/j.chemolab.2023.104825.

Goel, P., Datta, A., and Mannan, M. S. 2017. Industrial Alarm Systems: Challenges and Opportunities. Journal of Loss Prevention in the Process Industries 50: 23–36. https://doi.org/10.1016/j.jlp.2017.09.001.

Google DeepMind. 2025. Gemma 3 Technical Report. [CITATION NEEDED, cite the Gemma 3 report with correct year and identifier]

Han, P. and Kim, M. 2014. Optimizing Leak Detection Performance. Paper presented at the PSIG Annual Meeting, Baltimore, Maryland, 6–9 May. PSIG-1407.

IEC. 2016. Functional Safety, Safety Instrumented Systems for the Process Industry Sector, Part 1, IEC 61511-1:2016. Geneva: International Electrotechnical Commission.

ISA. 2016. Management of Alarm Systems for the Process Industries, ANSI/ISA-18.2-2016. Research Triangle Park, North Carolina: International Society of Automation.

Jessen, H. and Roshchin, M. 2025. Agentic AI Revolution Across Oil and Gas Value Streams. Paper SPE-229240-MS presented at ADIPEC. [CITATION NEEDED, verify location and dates]

Jocher, G., Chaurasia, A., and Qiu, J. 2023. YOLOv8 by Ultralytics. https://github.com/ultralytics/ultralytics.

Korjani, M., Conley, D., and Smith, M. 2024. Temporal Deep Learning Image Processing Model for Natural Gas Leak Detection Using OGI Camera. Paper OTC-34756-MS presented at the Offshore Technology Conference Asia. [CITATION NEEDED, verify location and dates]

Laberge, J. C., Bullemer, P., Tolsma, M. et al. 2014. Addressing Alarm Flood Situations in the Process Industries Through Alarm Summary Display Design and Alarm Response Strategy. International Journal of Industrial Ergonomics 44 (3): 395–406. https://doi.org/10.1016/j.ergon.2013.11.008.

Liang, J., Liang, S., Zhang, H. et al. 2024. Leak Detection in Natural Gas Pipelines Based on Unsupervised Reconstruction of Healthy Flow Data. SPE Prod & Oper 38 (3): 513–526. [CITATION NEEDED, verify pagination, SPE paper number and DOI. The earlier draft cited this as SPE Journal; it appeared in SPE Production & Operations]

Malhotra, P., Ramakrishnan, A., Anand, G. et al. 2016. LSTM-Based Encoder-Decoder for Multi-Sensor Anomaly Detection. arXiv:1607.00148 (preprint, submitted 1 July 2016).

Murvay, P.-S. and Silea, I. 2012. A Survey on Gas Leak Detection and Localization Techniques. Journal of Loss Prevention in the Process Industries 25 (6): 966–973. https://doi.org/10.1016/j.jlp.2012.05.010.

Narkhede, P., Walambe, R., Mandaokar, S. et al. 2021. Gas Detection and Identification Using Multimodal Artificial Intelligence Based Sensor Fusion. Applied System Innovation 4 (1): 3. https://doi.org/10.3390/asi4010003.

Narkhede, P., Walambe, R., Chandel, P. et al. 2022. MultimodalGasData: Multimodal Dataset for Gas Detection and Classification. Data 7 (8): 112. https://doi.org/10.3390/data7080112.

Page, E. S. 1954. Continuous Inspection Schemes. Biometrika 41 (1/2): 100–115. https://doi.org/10.1093/biomet/41.1-2.100.

Sabbagh, V. B., Lima, C. B. C., and Xexéo, G. 2024. Comparative Analysis of Single and Multiagent Large Language Model Architectures. SPE J. 29 (12): 6869–6884. [CITATION NEEDED, verify issue and SPE paper number]

Santiago, C. J. S., Shumaker, N., and Weir, A. 2025. Integrating Data-Driven Insights with Domain Expertise Using Agentic Conversational Analytics. Paper SPE-228143-MS presented at the SPE Annual Technical Conference and Exhibition. [CITATION NEEDED, verify location and dates]

Sharma, A., Kumar, R., Singh, P. et al. 2024. Gas Detection and Classification Using Multimodal Data Based on Federated Learning. Sensors 24 (18): 5904. https://doi.org/10.3390/s24185904. [CITATION NEEDED, verify author list]

Vergara, A., Vembu, S., Ayhan, T. et al. 2012. Chemical Gas Sensor Drift Compensation Using Classifier Ensembles. Sensors and Actuators B: Chemical 166–167: 320–329. https://doi.org/10.1016/j.snb.2012.01.074.

Wang, Z., Schaul, T., Hessel, M. et al. 2016. Dueling Network Architectures for Deep Reinforcement Learning. Proc., 33rd International Conference on Machine Learning (ICML), New York City, 19–24 June, 1995–2003.

Zhang, E. and Zhang, E. 2025. Gas Pipeline Leakage Detection Based on Multiple Multimodal Deep Feature Selections and Optimized Deep Forest Classifier. Frontiers in Environmental Science 13: 1569621. [CITATION NEEDED, verify article number]

Zhang, J., Hoffman, A., Murphy, K. et al. 2013. Review of Pipeline Leak Detection Technologies. Paper presented at the PSIG Annual Meeting, Prague, Czech Republic, 16–19 April. PSIG-1303.

## Appendix A. Items Still Requiring Author Action

This appendix is a working list for the authors and is not intended for publication. Every result in the body of the manuscript is backed by a stored result file.

A.1 Cannot be resolved without data not currently on disk.

- Perception split (Section 3.3, Table 4). data/Thermal Camera Images is empty in the working tree, and the only frames present anywhere are 83 Mixture images (one of them zero bytes) in a partial download folder. The randomized image split therefore could not be replaced with a block-wise one. Restore the images, re-split block-wise, re-report. If accuracy falls, that is a reportable result and it supports the paper’s own argument rather than undermining it. A.2 Recommended before submission.

- Re-select the deployed cost ratio on a held-out validation split rather than on test-partition dispersion (Section 4.4).

- Implement and evaluate an ordinal or cost-matrix objective that prices under-escalation and over-escalation differently (Section 5.3). This is where the paper’s own evidence points and is probably the strongest single addition available.

- Reliability diagrams for the four calibration estimators. Section 4.7 reports ECE with adaptive bins, bootstrap intervals, a bin sweep, class-conditional ECE, Brier score and NLL, but not the diagrams themselves.

- Raise the run count from 5 to at least 29 randomized runs and add an equivalence analysis over a region of practical equivalence, so a positive claim of practical equivalence can be made instead of a disclaimer about power (Section 3.6).

- Reconcile the false-alarm denominator across the codebase. retrain/metrics.py divides false alarms by the number of alerts; this manuscript divides by the number of clean windows. They agree only at zero, and only the latter converts to alarm burden.

- Confirm the corpus acquisition interval from Narkhede et al. (2022), since the per-hour alarm-burden translation in Section 4.6 rests on it. The per-1,000-window figures do not.

- Decide whether an on-device evaluation belongs in this paper at all. It was removed here because none was performed. If one is added later it needs its own protocol, and the safety columns must be reported on the corrected pipeline rather than carried over.

- Resolve every [CITATION NEEDED] in the reference list, and confirm that Liang et al. (2024) is cited to SPE Production & Operations rather than SPE Journal.

A.3 Terminology, resolved here but needing author sign-off. The earlier draft described the decision component as trained by offline reward-shaped reinforcement learning, with an asymmetric reward, ε-greedy action selection, replay episodes, cumulative reward and a Huber loss. The model behind every number in this paper is trained by cost-weighted cross-entropy against targets from the deterministic map a*(·), as set out in Section 3.3 and Eq. 2. The description here is the correct one. All reinforcement-learning language and the associated training-dynamics figure have been removed, and this correction should carry explicit sign-off from all three authors.

## Appendix B. Reproducibility

Pipeline. Windows of length 20 formed over the raw corpus, with windows spanning a class boundary discarded, giving 6,324 windows at 1,581 per class. The anomaly feature is the mean reconstruction error of the full 20-step window under the pretrained NoGas autoencoder. The block-wise holdout reserves a contiguous 20% of each class block for test, separated from both training segments by a 20-window embargo, with the held-out block’s position drawn from the run seed. Feature standardization and anomaly-percentile normalization are fitted on the training partition only. In the leave-one-class-out experiment they are fitted on the three training classes only, so no statistic of the withheld class enters training.

Protocol. Five seeds (42, 1337, 7, 2024, 99), each with its own partition. PyTorch determinism guards enabled, single-threaded execution. Each experiment in Sections 4.1 to 4.7 was executed in a single uninterrupted run.

Artifacts. retrain/safety_metrics.py (metric set and Clopper-Pearson bounds); retrain/new_baselines.py (k-NN, threshold rule, CUSUM); retrain/run_all_v2.py (model comparison, cost sweep, perturbation, ablation, anomaly evaluation); retrain/run_loco_v3.py (leave-one-class-out with three-class scaling); retrain/run_calib_actions_v2.py (calibration, action-selection matrices, ROC curves); retrain/run_anomaly_influence.py (anomaly-input sensitivity); retrain/make_figs_v2.py (Figs. 1 to 16). Results in retrain/results_v2/: v2_zoo.csv, v2_zoo_sig.json, v2_loco.csv, v2_costsweep.csv, v2_perturb.csv, v2_ablation.csv, v2_anomaly.json, v2_calibration.csv, v2_calibration_perseed.csv, v2_calibration_binsweep.csv, v2_action_matrix.csv, v2_roc.json, v2_anomaly_influence.csv.

Figure palette. Categorical colors were checked against colorblind-separation, chroma, lightness and contrast criteria. The green and orange pair sits in the marginal separation band, so every categorical mark also carries a direct value label as a second channel of encoding.

## Appendix C. Author Verification Items

Five points could not be settled from the manuscript or from the code that produced the results, and need confirmation before submission. They are separated from Appendix A because these are questions of fact or intent rather than work items.

- Operational meaning of Action 2. The evaluation code counts escalation as a ≥ 3 and under-escalation as a ∈ {1, 2}, so Request verification was measured as a sub-alarm response that does not notify an operator. Table 3 has been corrected to match. If the intended design is that Request verification does place a notification in front of an operator, then the escalation boundary in safety_metrics.py is wrong rather than the table, and Sections 4.3, 4.6, 5.1 and 5.2 would all need recomputing against a ≥ 2. Confirm which is intended.

- Acquisition interval. The corpus as distributed carries no timestamp column, so the interval between consecutive readings cannot be established from the data. Every per-hour alarm figure in Section 4.6 is presented as an illustration conditioned on one window every 2 s. Confirm the true interval from the acquisition protocol, or drop the hourly illustration entirely and keep only the per-1,000-window quantity.

- Model subsets. The recurrent network and conservative Q-learning appear in the in-distribution comparison but not in the leave-one-class-out grid. Confirm whether that was deliberate or an omission, and whether the grid should be extended.

- Historical cost-ratio selection. The deployed ratio of 8:1 is not the accuracy optimum, and the earlier project record indicates it was chosen on test-partition dispersion. The sweep reported in Section 4.4 does not depend on that choice, but the description of how the deployed configuration was arrived at does. Confirm the chronology.

- References marked [CITATION NEEDED]. Nine entries carry bibliographic details that could not be verified from the material available. None is load-bearing for a result, but each needs checking before submission, in particular the venue for Liang et al. (2024), which the earlier draft cited to SPE Journal and which appears to have been published in SPE Production and Operations.